## Read Me
VMI Data Center Load Calculation Tool
Purpose
A free planning-stage tool to estimate connected load, demand load, and rough UPS/DG/battery sizing for a data center or data hall — built by Vision Matrix Institute (visionmatrixinstitute.com) as a learning resource and a preview of the calculation logic taught in the Data Center Electrical Design Specialist course.
How to use it
1. Go to the 'Load Calculator' tab. Replace the example equipment list (blue text) with your own project's loads.
2. Adjust the yellow-highlighted assumption cells (diversity factors, PUE, safety margins) to match your project.
3. Read the Totals, UPS Sizing, DG Sizing, and Battery Sizing sections — they update automatically.
Color legend
Blue text = an input cell you should edit for your own project.
Black text = a formula — do not overtype these, or the sheet will stop calculating.
Yellow fill = a key assumption worth double-checking against your actual project/site conditions.
Important disclaimer
This is a planning-stage estimation tool for learning purposes, using simplified industry rule-of-thumb methods. It is NOT a substitute for a detailed engineering study performed against the applicable IS/IEC/NFPA standards for your project, and all outputs must be verified by a qualified electrical engineer before any procurement or design decision. This is exactly the kind of calculation covered in full engineering depth inside VMI's Data Center Electrical Design Specialist course.
Want the full picture?
This tool covers Steps 1-5 of a real data center electrical design. Our course covers this end-to-end: SLD preparation, transformer & UPS design, DG systems, cable & busduct sizing, earthing & lightning protection, short-circuit studies in ETAP, and Revit MEP/BIM coordination — taught live by practicing engineers. Learn more at visionmatrixinstitute.com.

## Load Calculator
DATA CENTER LOAD CALCULATION WORKSHEET
Edit the blue example rows below to match your own project. Diversity factors and category labels are typical planning-stage values — verify against your project specifics.
STEP 1 — LIST YOUR LOADS
# | Load / Equipment Description | Category | Qty | Unit Rating (kW) | Connected Load (kW) | Diversity Factor | Demand Load (kW)
1 | IT Rack — 6kW average server rack | IT Load | 40 | 6 | 240 | 0.9 | 216
2 | IT Rack — high-density GPU/AI rack | IT Load | 8 | 15 | 120 | 0.9 | 108
3 | CRAC/CRAH cooling unit | Cooling | 6 | 35 | 210 | 0.8 | 168
4 | Chiller plant (if applicable) | Cooling | 2 | 90 | 180 | 0.7 | 126
5 | Data hall general lighting | Lighting | 1 | 12 | 12 | 0.9 | 10.8
6 | Emergency / egress lighting | Lighting | 1 | 3 | 3 | 1 | 3
7 | UPS system losses (typ. 6-8% of IT load) | UPS Losses | 1 | 25 | 25 | 1 | 25
8 | PDU / busway distribution losses | Distribution Losses | 1 | 8 | 8 | 1 | 8
9 | Fire pump / fire suppression system | Life Safety | 1 | 22 | 22 | 0.3 | 6.6
10 | Office / admin area HVAC | Auxiliary | 1 | 15 | 15 | 0.7 | 10.5
11 | Security systems (CCTV, access control, BMS) | Auxiliary | 1 | 6 | 6 | 0.9 | 5.4
12 | Elevators / lifts | Auxiliary | 1 | 11 | 11 | 0.4 | 4.4
13 | Miscellaneous / spare capacity | Auxiliary | 1 | 10 | 10 | 1 | 10
| TOTAL |  |  |  | 862 |  | 701.7
STEP 2 — FACILITY-LEVEL SUMMARY (PUE CHECK)
Total Connected Load (kW) |  |  |  |  | 862
Total Demand Load (kW) |  |  |  |  | 701.7
IT Load Only, Demand Basis (kW) |  |  |  |  | 324
Assumed PUE (Power Usage Effectiveness) |  |  |  |  | 1.6
Estimated Total Facility Power via PUE (kW) |  |  |  |  | 518.4
PUE 1.5-1.8 is typical for a well-run enterprise data center; hyperscale facilities often achieve 1.2-1.4.
STEP 3 — UPS SIZING (ESTIMATE)
Total Demand Load To Be Protected (kW) |  |  |  |  | 701.7
UPS Safety / Growth Margin (%) |  |  |  |  | 25%
Assumed UPS Output Power Factor |  |  |  |  | 0.8
Recommended UPS Rating (kVA) |  |  |  |  | 1096.4062
STEP 4 — STANDBY DG SIZING (ESTIMATE)
Total Demand Load To Be Backed Up (kW) |  |  |  |  | 701.7
DG Safety / Starting-Load Margin (%) |  |  |  |  | 40%
Assumed DG Output Power Factor |  |  |  |  | 0.8
Recommended DG Set Rating (kVA) |  |  |  |  | 1227.975
DG margin is higher than UPS margin to account for motor starting (inrush) currents from chillers/pumps.
STEP 5 — BATTERY BACKUP SIZING (SIMPLIFIED ESTIMATE)
UPS Load To Be Backed Up (kW) |  |  |  |  | 701.7
Required Backup Time (minutes) |  |  |  |  | 15
Battery System DC Voltage (V) |  |  |  |  | 480
Inverter Efficiency (fraction) |  |  |  |  | 0.92
Estimated Required Battery Capacity (Ah) |  |  |  |  | 397.2486
This is a simplified planning estimate — see the cell comment on the result for what it does not account for. Final battery selection should use manufacturer discharge-curve data.
Built by Vision Matrix Institute — visionmatrixinstitute.com — as a free companion to the Data Center Electrical Design Specialist course. Not a substitute for a licensed engineer's detailed design.
Note on F52: Simplified estimation formula: Ah = (Load_kW x 1000 x (Backup_min/60)) / (DC_Voltage x Inverter_Efficiency). For final design, use manufacturer battery discharge curves at your actual load and end-voltage — this rule-of-thumb does not account for battery aging, temperature derating, or discharge-curve non-linearity.